CAPITAL INVESTMENT PLAN FOR

2013-15

BY

Power System Control & Automation

TATA POWER DELHI DISTRIBUTION LIMITED

CENNET SCADA building, Netaji Subhash Place,

Pitampura, New Delhi

December, 2011

Contents

CHAPTER – 1	3

BACKGROUND	3

1.1	TPDDL PROFILE	4

1.2	JOURNEY TOWARD EXCELLENCE	5

CHAPTER – 2	8

POWER SCENARIO IN DELHI	8

2.1	ENERGY REQUIREMENT AND PEAK DEMAND	9

2.2	POWER SCENARIO FOR TPDDL AREA	9

CHAPTER – 3	11

CAPITAL INVESTMENT MADE DURING MYT PERIOD 2007-11	11

3.1	CAPITAL INVESTMENT DURING MYT PERIOD: FY 2007-08 to FY 2010-11	12

3.2	DETAILS OF CAPITAL INVESTMENT INCURRED	14

3.2.1	AT&C LOSS REDUCTION:	14

(a) METERING SYSTEM	14

(b)   HIGH VOLTAGE DISTRIBUTION SYSTEM (HVDS)	15

(c)   REPLACEMENT OF LT BARE CONDUCTOR WITH LT CABLE	15

3.2.2	SYSTEM RELIABILTY IMPROVEMENT	17

(a)	GRID SUBSTATION AUTOMATION	18

(b)	COMMUNICATION NETWORK	19

(c )	SCADA IMPLEMENTATION	20

(d)	DISTRIBUTION MANAGEMENT SYSTEM (DMS)	20

(e)	DISTRIBUTION AUTOMATION	21

(f)	OUTAGE MANAGEMENT SYSTEM (OMS)	22

(g)	GEOGRAPHICAL MANAGEMENT SYSTEM (GIS):	23

(h)	 REPLACEMENT OF SICK CABLES	23

(i)	OTHER SYSTEM IMPROVEMENT WORKS	23

3.2.3	SYSTEM RELIABILITY INDICES	24

a.	AVERAGE SYSTEM AVAILABILITY INDEX (ASAI)	24

b.	SYSTEM AVERAGE INTERRUPTION FREQUENCY INDEX (SAIFI)	24

c.	SYSTEM AVERAGE INTERRUPTION DURATION INDEX (SAIDI)	25

3.2.4	LOAD GROWTH	26

3.2.5 INFRASTRUCTURE DEVELOPMENT	27

CHAPTER – 4	29

POWER SCENARIO         FY 2013-15	29

4.1	POWER SCENARIO IN NEAR FUTURE:	30

CHAPTER – 5	33

CAPITAL INVESTMENT PROPOSED FOR MYT PERIOD 2013-15	33

5.1	TARGET AREA-WISE DISTRIBUTION OF CAPEX:	35

5.1.1	CAPEX FOR LOAD GROWTH	37

5.1.1.1	 NEW METERS	37

5.1.1.2  NEW GRIDS	38

5.1.1.2	 AUGMENTATION OF EXISTING GRIDS	38

5.1.1.3	 AUGMENTATION OF 11 KV NETWORK	39

5.1.2	CAPEX FOR AT&C LOSS REDUCTION	41

5.1.2.1	REPLACEMENT OF METERS	41

5.1.2.2	LTABC and HVDS WORKS	42

5.1.3	CAPEX FOR RELIABILTY IMPROVEMENT	44

5.1.3.1	NEW TECHNOLOGIES	44

5.1.3.2	 SAFETY RELATED	52

5.1.3.3	11 kV SICK CABLE REPLACEMENT	52

5.1.3.4 	PROTECTION & TESTING OF INSTRUMENTS	53

5.1.4	CREATION OF INFRASTRUCTURE FACILITIES AND ADMINISTRATIVE BUILDING	54

5.2	CAPITALIZATION SCHEDULE	56

5.3	FINANCING PLAN	57

CHAPTER – 6	58

QUALITY IMPROVEMENT PLAN	58

6.1	 TRANFORMER & FEEDER FAILURE RATE	59

6.2	FREQUENCY VARIATIONS:	60

6.3	VOLTAGE UNBALANCE:	60

# CHAPTER – 1

# BACKGROUND

# 1.1	TPDDL PROFILE

TATA Power Delhi Distribution Limited (TPDDL), a joint venture between Tata Power and the Government of NCR of Delhi had taken over the distribution of electric power in the area of Delhi Vidyut Board (DVB) w.e.f. 1st July 2002 as part of the distribution sec-tor reform process.. With a registered consumer base of around 11.84 lakhs and a peak load of around 1313 MW, the company's operations span across an area of 510 sq kms. The daily average energy requirement of TPDDL is about 20 MUs, with annual energy requirement of around 7316 MUs.

For administrative purpose TPDDL is split into 50 zones comprising of 20,000 – 25,000 consumers each. TPDDL also maintains the street light in its area on behalf of Road owning/Revenue agencies. The various consumer touch points include Consumer Care Centers (12 Nos.), Zonal Centers (50 Nos.), Business District offices (12 Nos.) and Consumer Call Centers. Table 1.1 below gives the list of 12 Business District Offices.

Table 1.1

| S. No | Business District Offices |
| --- | --- |
| 1 | Bawana |
| 2 | Narela |
| 3 | Rohini |
| 4 | Mangolpuri |
| 5 | Shalimar Bagh |
| 6 | Badli |
| 7 | Shakti Nagar |
| 8 | Civil Lines |
| 9 | Model Town |
| 10 | Keshav puram |
| 11 | Moti Nagar |
| 12 | Pitam pura |

# 1.2	JOURNEY TOWARD EXCELLENCE

TPDDL has consistently over-achieved its targets and over a short span of 9 years brought down the AT&C loss level from 53% to below 14% along-with major improvements in reliability of network and consumer services. TPDDL is the only Indian utility to be conferred the Edison Electric Institute (USA) awards for GIS implementation (2008) and for Policy Advocacy (2009), BSC Hall of Fame (2008) instituted by Prof. Norton & Kaplan, Asian Power Utility of the year Award consecutively for last four years and the Ministry of Power Govt. of India Award for meritorious performance for three out of last four years.

TPDDL is a Utility which supplies electricity through its distribution network at regulated tariffs to all consumers in its licensed area. TPDDL, in order to partly meet its consumers demand has established a 108MW combined cycle gas based power plant in its licensed area (Rithala).

TPDDL has been in the forefront in the adoption of latest technology in the utility sector. Together with its culture of Consumer Service Excellence, Continuous Learning, Performance Orientation, Innovation and empowerment, it has been able to set benchmarks of accelerated reduction of AT&C losses (~75%) and enhance consumer satisfaction. TPDDL leadership evolved an inspiring Vision and Mission in 2002-03, which has been revisited periodically and revised in 2008.

Growth plans of TPDDL includes increasing the activity base within licensed area  and complimenting Tata Power’s growth plan into distribution business Internationally/Nationally. In order to capitalize on its core competency, increase employee engagement & enrichment it has made foray into IT& SCADA consultancy although it has low revenue potential compared to the distribution business. TPDDL has adopted Climate Change Policy in line with Tata Group’s Climate Change Policy.

TPDDL, in the last five years, has been the front-runner in implementing power distribution reforms and has made persistent efforts to become a consumer centric, value driven organization. Systems such as Supervisory Control And Data Acquisition (SCADA), Geographic Information System (GIS), Operator Training Stimulator (OTS) and OMS (Outage Management System) are the cornerstone of the company's distribution automation project. To fight the menace of power theft, modern techniques like Temper proof meters, High Voltage Distribution (HVDS) System and LT Arial Bunch Conductor have been adopted. Since privatization, the AT&C losses in TPDDL areas have shown a record decline. TPDDL has reduced the AT&C losses by 44.25% in 5 years (from 23.73% in FY 2006-07 down to below 14% in FY 2010-11). The introduction of breakthrough technologies, structured maintenance schedules and dynamic organization structure have ensured remarkable improvement in the power supply situation manifested by the significant improvement in Reliability Indices such as SAIDI & SAIFI. Further TPDDL has embarked upon an ambitious plan to implement high-tech automated systems for its entire distribution network.

TPDDL has in the last five years introduced several breakthrough concepts in Consumer Service such as Sharing of 100% consumers’ billing database on website, Automatic Meter Reading; SMS based fault management system, 24x7 operational stores, Door step offering for new connection, Quarterly Independent Consumer Satisfaction Survey, Gift Electricity Scheme ‘Urja’, etc.

TPDDL initiated several measures to enhance the quality of the network and took proactive measures in the growth areas which in turn improved the overall system performance. Various system studies were conducted by CEA, KEMA and Cyme and recommendations were received for establishment of new grid substations, augmentation of power transformers, renovation of existing grid & distribution substations, addition of shunt capacitors, etc. These studies and audits have been the basis of capital expenditure made in the last five years.

The company has set up the Centre for Power Efficiency in Distribution (CENPEID), the first institute for skill accreditation and certification for the power distribution sector in India. The Institute is slated be a national resource and shall cater to the skill and management training needs of the sector as a whole.

# CHAPTER – 2

# POWER SCENARIO IN DELHI

# 2.1	ENERGY REQUIREMENT AND PEAK DEMAND

The energy requirement in of Delhi during 2010-11 was 24437 MUs as against 22370 MU during 2007-08, whereas the peak demand during the same period has increased from 4030 MW to 4720 MW during the same period.  Table – 2.1 shows the requirement of energy, and peak demand in the year 2003-04 and 2006-07.

It may be noted that in Delhi region, the peak demand is growing at a higher pace as compared to the energy requirement. Besides other reasons, this phenomenon can be attributed to growing urbanization, changes in life style and efficiency improvement (in terms of reduction in losses) in the distribution system.  Specifically in case of Delhi, the reduction in losses has led to suppressed increase in energy requirement, whereas the higher penetration of electronic appliances (due to growing urbanization) have led to higher increase in the peak demand during the past few years. It can be substantiated from the Table – 2.1 which summarizes the energy and peak requirement in Delhi during the period 2007-11

Table – 2.1

| Demand Supply situation in Delhi |  |  |  |  |
| --- | --- | --- | --- | --- |
| Year | Peak Demand Met (MW) | % Change | Energy Requirement Met (MU) | % Change |
| 2007-08 | 4030 |  | 22370 |  |
| 2008-09 | 4036 | 0.15% | 22006 | -1.63% |
| 2009-10 | 4408 | 9.22% | 23358 | 6.14% |
| 2010-11 | 4720 | 7.08% | 24437 | 4.62% |

# 2.2	POWER SCENARIO FOR TPDDL AREA

Similar trend has been observed in the TPDDL area. The peak demand in TPDDL area is growing consistently over the past few years. For instance, peak demand in TPDDL area has increased from 1068 MW to 1286 MW during the period FY 07-08 to FY 10-11.

Table - 2.2

| Energy Profile |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S. No. | Year | Energy Input (MUs) | % Change | Energy consumption (MUs) | % Change | AT&C Losses (%) | Peak Demand (MW) | % Change |
| 1 | 2007-08 | 6276 |  | 4975 |  | 18.31 | 1068 |  |
| 2 | 2008-08 | 6370 | 1.50% | 5161 | 4% | 15.41 | 1140 | 7% |
| 3 | 2009-10 | 6910 | 8.48% | 5800 | 12% | 14.47 | 1212 | 6% |
| 4 | 2010-11 | 7316 | 5.88% | 6400 | 10% | 13.1 | 1286 | 6% |

The Table – 2.3 shows the billed consumption (in MUs) to different consumer categories in TPDDL system from 2007-08 to 2010-11.  As seen in the Table – 3.3, the billed consumption has increased at the rate of 7.05 % in domestic category, 8.95 % in non domestic category, 2.58 % in industry and 8.26 % in other consumer categories.

Table – 2.3

| Consumer category-wise billed consumption |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Consumer Category | 2007-08 | 2008-09 | 2009-10 | 2010-11 | 2011-12 | CAGR |
| Domestic | 2027 | 2102 | 2447 | 2752 | 2849 | 7.05% |
| Non-Domestic | 933 | 1014 | 1176 | 1307 | 1432 | 8.95% |
| Industry | 1744 | 1767 | 1884 | 1962 | 1981 | 2.58% |
| Other | 271 | 279 | 293 | 379 | 403 | 8.26% |
| Total | 4975 | 5161 | 5800 | 6400 | 6665 | 6.02% |

# CHAPTER – 3

# CAPITAL INVESTMENT MADE DURING MYT PERIOD 2007-11

# 3.1	CAPITAL INVESTMENT DURING MYT PERIOD: FY 2007-08 to FY 2010-11

Capital investments were made under the following benefit centers:

- AT&C loss reduction

- System Reliability Improvement

- Growth development plan for meeting the load growth

- Creation of infrastructure facilities including administration buildings

The expenditures made from FY 2007-08 to FY 2010-11 have been summarized in Table - 3.1:

Table – 3.1

| CAPEX EXPENDITURE INCURRED FROM FY 2007- 11 (in Rs Cr) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Job Heads | 2007-08 | 2008-09 | 2009-10 | 2010-11 | TOTAL |
| A | AT&C Loss Reduction | 111 | 148 | 128 | 103 | 490 |
| B | Reliability Improvement | 41 | 24 | 94 | 118 | 277 |
| C | Load Growth | 78 | 101 | 120 | 223 | 522 |
| D | Infrastructure Development | 15 | 16 | 32 | 21 | 83 |
| GRAND TOTAL |  | 245 | 288 | 374 | 465 | 1372 |

The details of year wise capital expenditure under different benefit heads from FY 2007-08 to 2010-11 is elaborated in chart – 3.1

Chart 3.1

The percentage of benefit head wise overall capital expenditure made from FY 2007-08 to FY 10-11 has been shown below:

Chart 3.2

# 3.2	DETAILS OF CAPITAL INVESTMENT INCURRED

For each of the above benefit centers, the prime investment heads are delineated below:

# 3.2.1	AT&C LOSS REDUCTION:

Major initiatives taken by TPDDL for reducing AT&C losses are mentioned below:

  - Metering systems

  - High Voltage Distribution Systems (HVDS)

  - Replacement of LT bare conductor with LT AB Cable.

# (a) METERING SYSTEM

TPDDL replaced the existing electro-mechanical meters with static meters which are tamper proof with almost no accuracy change with passage of time as these do not have moving parts. Further these meters are having features to record power factor, demand etc. The details of electrostatic meters installed from 2007 to 2011 are given in table 3.2 below:

Table – 3.2

| Year | Electronic Meters Installed |
| --- | --- |
| 2007-08 | 186246 |
| 2008-09 | 300376 |
| 2009-10 | 294966 |
| 2010-11 | 201573 |
| TOTAL | 983161 |

The year-wise capital expenditure incurred towards metering system during the MYT period 2007-11 is given in table 3.3 below:

Table - 3.3

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2007-08 | 76.0 |
| 2008-09 | 78.0 |
| 2009-10 | 78.0 |
| 2010-11 | 61.0 |
| TOTAL | 293.0 |

# (b)   HIGH VOLTAGE DISTRIBUTION SYSTEM (HVDS)

Under HVDS, the existing LT network in theft prone areas is replaced by HT network and new small capacity transformers are installed, which are nearer to the load centers and cover reduced no. of consumers. HVDS also enhances reliability by localizing faults and contribute to better quality of supply by eliminating the need for long low-tension lines.  The HVDS system reduces systems technical losses, and has thus helped TPDDL to meet the AT&C loss reduction targets.

In the first phase HVDS was planned in theft prone areas and new growth areas.  All new electrifications have been installed on HVDS to the extent possible.

However, it is seen that in areas infested with anti-lawful elements, direct tappings are being taken from transformer bushing despite all technical attempts to stop the same including welding metal boxes, applying hardened putty to the terminals etc. No law & order support has been able to provide & facilitate respite and such rampant un-lawful tappings are multiplying now, in some of the select areas.

# (c)   REPLACEMENT OF LT BARE CONDUCTOR WITH LT CABLE

The replacement of LT bare conductor lines results in reduced direct hookings done on bare LT conductor lines. Although there is no reduction of any technical losses due to installation of LT AB cable lines, the commercial losses get considerably reduced.

Such replacements of LT bare conductor with LT AB Cables have been done in the theft prone areas where direct hookings of bare LT lines were observed.

While this has brought about an overall positive impact, there are, however, areas where such cables have been destroyed and tapings restored.

The year-wise capital expenditure incurred for HVDS and LTABC works during the MYT period 2007-11 is given in table 3.4 below:

Table 3.4

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2007-08 | 35.0 |
| 2008-09 | 70.0 |
| 2009-10 | 50.0 |
| 2010-11 | 42.0 |
| TOTAL | 197.0 |

The cumulative expenditure made for AT&C loss reduction Vs actual reduction in AT&C losses is shown below:

Chart – 3.3

TPDDL was mandated to reduce AT&C losses from over 23.73 %  to the targeted value of 17% during the period 2007-11. Through its persistent efforts TPDDL has surpassed all records and as against a committed target reduction of 6.73%  in 4 years, TPDDL has reduced AT&C losses by about 10.6% in these 4 years.

A comparison of the targeted value as against achieved Loss reduction figures is mentioned below:

Chart – 3.4

# 3.2.2	SYSTEM RELIABILTY IMPROVEMENT

Reliability and Quality of supply has been another important factor on which TPDDL has primarily focused in the last four years. Extensive studies have been carried out in consultation with KEMA and using special analysis tools like Cyme, PSAF etc to understand the reliability needs of the system. The concept of N-1 reliability has been implemented at 11 kV, 33kV and 66 kV level. Many types of equipment which existed in highly depleted condition and were assessed to be non-repairable have been replaced by new state-of-art equipments. The old existing equipments were obsolete and used to break down frequently resulting in long outage durations. The new equipments are SCADA compatible and can facilitate remote operations for future requirements.

Major new technology initiatives taken by TPDDL for improving reliability are mentioned below:

  - Grid Substation Automation

  - Communication Network

  - SCADA Implementation

  - Distribution Management system

  - Distribution Automation

  - Outage Management System (OMS)

  - Geographical Information System (GIS)

# (a)	GRID SUBSTATION AUTOMATION

The main objective of the project was to make the 66/33/11 KV grid stations  compatible for SCADA system. This required replacing old grid station’s control and relay panels due to following constraints

- The control and relay panels were equipped with mechanical switches for control of breakers and electromechanical relays for protection.  The control was possible only locally (manually) and relay’s information was limited.

- Remote operation of grids from central location was not possible due to inadequate information and unavailability of relevant network data from grid stations due to absence of smart IEDS.

- Delay in identification of faulty section and restoration of supply. A LT level fault at times was leading to tripping of grid station incomers due to non coordination between different tripping devices; hence large area was subjected to supply failure.

# (b)	COMMUNICATION NETWORK

TPDDL had fundamental communications requirements to support operation services (SCADA) as well as enterprise services like Geographical information system (GIS), internet, Enterprise resource applications (SAP), Commercial and Billing applications etc.

TPDDL chose to deploy own private optical networks making use of the important asset already available  e.g. existing fiber network of TTSL & VSNL  in TPDDL licensed area and the right of way along TPDDL power transmission lines. The optical fiber technology selected is able to accommodate as a minimum, the defined functional requirements of adequate bandwidth capacity, latency within specified limits designed to meet the most stringent requirement, such as protective relaying, and network availability with required redundancy.

# (c )	SCADA IMPLEMENTATION

The objective of SCADA project was to acquire network data, monitor and control sub transmission system consisting of 56 Grid stations from a central location.  SCADA   system is based on redundant system design with main server and hot standby servers in Main Control Centre (MCC) and to meet any disastrous situation, the Backup Control Centre (BCC) has been setup with same functionality at a different location i.e. Inderpuri.

Besides having generic functionalities like alarm, tagging, trends management, the SCADA system have been deployed with additional applications to use system data for effective monitoring of sub transmission network. These applications are

- Load shedding application –   	To shed load in blocks

- To shed load in case of under frequency

- To shed load in case of over loading

- Load forecasting Application  - 	To forecast next day load demand

# (d)	DISTRIBUTION MANAGEMENT SYSTEM (DMS)

Main objective of DMS project is to establish Centralized monitoring system for entire 11 KV networks of TPDDL for coordination with all zones for faster restoration of Network.

Prior to deployment of DMS ,  TPDDL distribution network  was managed at zonal level all operation were  carried out by zonal engineers and network real-time data was  not available , this led  to following -

- Absence of knowledge for shifting of load to other feeder due to Overloading of feeder.

- Absence of Network reconfiguration/ back feeding of network loads on inter-zonal feeders in case of acute emergencies like complete bus/grid outage.

- Unintentional overloading of sections due to back-feeding only based on prevalent practices. Network Knowledge is person specific and efficiency depends on his retention skills.

- Inadequate utilization of network.

Presently in districts   where DMS has been implemented the network decisions are taken by control centre executives with all information to suggest optimal way of handling any network contingency.

# (e)	DISTRIBUTION AUTOMATION

Distribution Automation is the field automation part of DMS wherein selected strategically located RMUs are automated to control from SCADA system. Main objective of distribution automation is to identify faulty section, isolate this section and restore the network from remote control centre in minimum possible time. Generally 15-20% of the whole network points are automated to reap full benefit of investment.

The selection of the automation points is critical exercise for any utility. In case of TPDDL, Network Planning and Analysis group using DRAKE software application identifies Automation points in distribution networks.. Distribution Automation involves –

- Motorisation of RMU isolators and Breaker to make them operational from SCADA system.

- Automation of RMU by placing Field remote terminal units (FRTU) at each identified substation.

- In case where only FPI status is to be monitored; point no. 1 does not hold.

- Communication of each FRTU with DA master or Data concentrator on GPRS, which in turn ,communicates with SCADA system

Major Milestones achieved during 10-11

- Deployed in 3 Distts i.e. Shakti Nagar, Model Town and Civil Lines.

- Deployed in areas where the 11 KV feeders emanate from DTL/BSES grids.

- Training of the various user groups.

# (f)	OUTAGE MANAGEMENT SYSTEM (OMS)

Outage management system is an automation solution interfaced with various systems in utility so as to ensure prompt restoration of the outages affecting customers, facilitate utility with accurate historical data on outages for improving work processes related to operations and maintenance.

After Implementation of OMS; all No supply calls from Unified Call Centre (UCC) are forwarded to OMS. The calls received at OMS aregrouped with pre defined configurable logics to  predict the probable faulty network component which has resulted into outage to customers and then an trouble order is created in OMS for  the zonal shift associate to attend outage .The call centre is kept updated through system (SAP ISU -OMS interface) w.r.t status and list of affected customers.

While closing the order, the dispatcher updates the details of follow up work required as per the feedback received from crew. The follow up work could be for replacement of service line/ brunt meter or immediate maintenance of any equipment. The follow up order is created in SAP-PM system and it will get added to the bin of the person/department responsible for that follow up work.

The OMS- SCADA/DMS interface is on ICCP to facilitate real time information flow from SCADA/DMS to OMS for list out the customer affected due to interruption at the 11 KV or sub transmission level. This information is made available to call centre almost on real time basis. In such event instead consumer calling TPDDL for lodging the complaint, TPDDL shall intimate customer about the outage and estimated restoration time.

# (g)	GEOGRAPHICAL INFORMATION SYSTEM (GIS):

TPDDL has Established GIS system for complete TPDDL area. All Assets such as transformers, Buildings, Poles, Cables etc have been mapped in the software. More then 10,00,000 consumers are also mapped on the system. The GIS system has been operational for from 2006 onwards.

GIS map were digitized using the satellite image followed by field survey which now contain network, customers, distribution transformers and other assets, land base etc. GIS map was ready by 2006.

GIS database contains spatial and attribute data of customers, electrical assets and land base covering the license area. GIS system has become the communication platform for various operations of TATA Power Delhi Distribution Ltd (TPDDL). The common information is being shared by all and integrated and optimum decisions are being taken. Additionally, with inbuilt potential of providing various analyses, decisions are efficient and better informed. Customer service as well as commercial functions is being better managed as GIS has been integrated with the Customer Relation Management Tool (CRM) for facilitating various tasks. The system is currently deployed with various user groups including commercial and operations. EGIS geo referenced data and built source data helps in creating distribution system operation model to automate and improve its operations by implementation of Distribution Management and Outage Management System.

# (h)		REPLACEMENT OF SICK CABLES

Old 11kV underground cables with history of frequent and a number of faults have been replaced to ensure reliable and continuous power supply. TPDDL has so far replaced more than 250 kM of underground cable network.

# (i)	OTHER SYSTEM IMPROVEMENT WORKS

Other works such as installation/replacement of Autoreclosers, LT ACB, old 11kV switchgears have been carried out to improve system reliability

The year-wise capital expenditure incurred towards reliability related works during the MYT period 2007-11 is given in Table 3.5 below:

Table 3.5

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2007-08 | 41.0 |
| 2008-09 | 24.0 |
| 2009-10 | 94.0 |
| 2010-11 | 118.0 |
| TOTAL | 277.0 |

# 3.2.3	SYSTEM RELIABILITY INDICES

# AVERAGE SYSTEM AVAILABILITY INDEX (ASAI)

Average System Availability Index is a measure of the overall reliability of the system. It represents the percentage of time during the year that the average customer has power. TPDDL has achieved ASAI of 99.93% in FY 10-11 as against 99.92% in FY 07-08.

Chart – 3.5

# SYSTEM AVERAGE INTERRUPTION FREQUENCY INDEX (SAIFI)

System Average Interruption Frequency Index is a measure of the number of times the average customer experiences an interruption in supply.  TPDDL has achieved SAIFI of 4.48 in FY 10-11 as against 5.48 in FY 07-08.

Chart – 3.6

# SYSTEM AVERAGE INTERRUPTION DURATION INDEX (SAIDI)

System Average Interruption Frequency Index is a measure of the average duration of interruption in supply which a customer experiences..  TPDDL has achieved SAIDI of 6.3 hrs in FY 10-11 as against 7.11 hrs in FY 07-08.

Chart – 3.7

Chart 3.8 below indicates reliability improvement achieved vs the cumulative investment.

Chart – 3.8

# 3.2.4	LOAD GROWTH

TPDDL experienced a load growth at rate of 7 % during last 4 years. To cater to this load growth TPDDL has added new grids as well as augmented 11 kV network. TPDDL since take over has added the following new grids:

Table - 3.6

| List of New Grids |  |  |
| --- | --- | --- |
| Year | 66 kV | 33 kV |
| 2007-08 | RG-24 | SMBFC |
| 2008-09 | Ghevra |  |
| 2009-10 |  | Tigipur |
| 2010-11 | Bhalaswa, DCI | DU, Kirti Nagar |
| 2011-12 |  |  |

In addition capacity of number of grids has been augmented to meet the growing demand.

TPDDL has also made the following additions to its network:

Table – 3.7

| Addition of sub-transmission and distribution lines from 2002-2007 |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.N. | Item | FY 02-03 | FY 07-08 | FY 10-11 |
| 1 | 33 kV and 66 kV OH/UG Lines (kM) | 332.5 | 549.2 | 705 |
| 2 | 11 kV OH/UG Lines(kM) | 2245 | 3191 | 3677 |
| 3 | LT Lines (kM) | 4172 | 5239 | 5749 |
| Addition of Transformation Capacity From 2002-20011 |  |  |  |  |
| 1 | Power Transformer (MVA) | 1651 | 2770 | 3209 |
| 2 | Distribution Transformers (MVA) | 1703 | 2988 | 4293 |

The year-wise capital expenditure incurred towards load growth during the MYT period 2007-11 is given in table 3.8 below:

Table – 3.8

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2007-08 | 78.0 |
| 2008-09 | 101.0 |
| 2009-10 | 120.0 |
| 2010-11 | 223.0 |
| TOTAL | 522.0 |

# 3.2.5 INFRASTRUCTURE DEVELOPMENT

TPDDL has upgraded its existing IT as well as administrative infrastructure to meet the aspiration of consumers as well as employees.

The year-wise capital expenditure incurred towards infrastructure development during the MYT period 2007-11 is given in table 3.9 below:

Table – 3.9

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2007-08 | 15.0 |
| 2008-09 | 15.0 |
| 2009-10 | 32.0 |
| 2010-11 | 21.0 |
| TOTAL | 83.0 |

# CHAPTER – 4

# POWER SCENARIO         FY 2013-15

# 4.1	POWER SCENARIO IN NEAR FUTURE:

The Master Plan for Delhi-2021, envisages a higher population growth in next 15 years through migration and natural growth in new areas like Bawana, Narela, Rohini etc. It has been highlighted in the plan that in order to cater to these new consumers; infrastructure has to be developed in a long term perspective. It is projected that future increase/growth will be both because of relocation/migration and natural growth. It is also envisaged that the land use pattern will continue to change in future which will have some impact on industrial and commercial activity. However, it needs to be highlighted that this phenomenon was prevalent in the past and to an extent gets captured in the Delhi growth rates on average. The projected energy profile of TPDDL for the Control Period 2012-13 to 2014-15 is given in Table – 4.1.

Table – 4.1

| Energy Profile |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| S. No. | Year | Energy Input (MUs) | Energy consumption (MUs) | AT&C Losses (%) | Peak Demand (MW) |
| 1 | 2012-13 | 8236 | 7222 | 12.75 | 1536 |
| 2 | 2013-14 | 8909 | 7829 | 12.50 | 1689 |
| 3 | 2014-15 | 9618 | 8483 | 12.25 | 1885 |

AT&C loss targets proposed by TPDDL are given in the table above. While TPDDL would undertake every effort to achieve the laid targets, the following factors may create hindrance with regard to the same:

The following factors make it difficult to achieve the aforesaid losses:

- The technical losses as on date stand at nearly 7%.

- External devices are now openly available in the market to tamper with the reading of electronic meters. Also, severe resistance is being faced from public regarding replacement of old electro mechanical meters. Meter tampering and erroneous reading through old electro mechanical meters contributes around 3 % of AT&C losses.

- Direct hooking in slum areas account for nearly  3 % of AT&C losses.

The above forecasts as listed in Table 4.1 have been prepared based on the factors like past growth trend in terms of electricity, macro-economic indices/factors, population and industrial growth with the demand for electrical energy is done to determine the future energy demand.

Table 4.2

| Proposed: Consumer category-wise expected billed consumption |  |  |  |
| --- | --- | --- | --- |
| Consumer Category | 2012-13 | 2013-14 | 2014-15 |
| Domestic | 3105 | 3385 | 3690 |
| Non-Domestic | 1589 | 1764 | 1941 |
| Industry | 2101 | 2227 | 2260 |
| Other | 427 | 454 | 482 |
| Total | 7222 | 7829 | 8483 |

However, it may be noted that the forecast does not take into account any special project or event that the city may see in the near future leading to a rapid/ abnormal acceleration of industrial and commercial activity in the licensed area or accelerated expansion of the residential sector. Also, the forecast has been made for “unrestricted” energy and load demand. The actual energy supply and peak demand “met” may be lower due to supply restrictions that necessitate load curtailment. Graphical representation of estimated inputs vs consumption for the period 2013-15 is depicted in Chart 4.1

Chart – 4.1

Chart – 4.2 shows estimated AT&C Losses in percentage against estimated energy input and consumption for the period of 2012 to 2015.

Chart – 4.2

# CHAPTER – 5

# CAPITAL INVESTMENT PROPOSED FOR MYT PERIOD 2013-15

To achieve the anticipated load growth and targeted AT&C loss reduction, TPDDL has carried out a detailed analysis of capital investment required for next four years. The analysis is based on various technical and physical audits carried out by TPDDL staff followed by discussions at various levels and review by senior management.

TPDDL Capex Plan, which is explained later in the chapter, is worked out after amalgamating the requirement at various levels. The total capital investment required at TPDDL for the control period 2013-15 is estimated at Rs. 1030 Cr.

The deployment of capital investment is proposed under the following benefit centers:

- Growth Development Plan to meet the load growth

- AT&C loss reduction

- System Reliability Improvement

- Creation of infrastructure facilities & administrative buildings

For each of the above benefit centers, the investment has been broken into the following sub-centers:

- AT&C loss reduction

        - Metering System

        - LT Aerial Bunched Conductor

- System Reliability Improvement

        - Automation

        - New Technologies

        - Safety related

        - 11 kV Sick Cable Replacement

- Growth Development Plan to meet the load growth

        - New grid sub-station

        - Augmentation of existing grids

        - Augmentation of 11 kV network

- Creation of Infrastructure Facilities & Administrative Buildings.

        - Administrative Buildings

        - Consumer Care Centers and Cash Collection Centers

        - Miscellaneous items like tools, communication equipment, testing lab etc.

# 5.1	TARGET AREA-WISE DISTRIBUTION OF CAPEX:

For improving the performance of TPDDL in terms of meeting the load growth, reduction of AT&C losses and reliability of supply, a detailed Capital Investment Plan has been worked out for the Control Period FY 12-15. The Capex Plan proposes an investment of Rs. 1030 Crores. The deployment of Capex is proposed under the following four benefit centers:

Load Growth				:	Rs. 658 Crores

AT&C Loss reduction		:	Rs. 138 Crores

Reliability				:	Rs. 133 Crores

Administration and Infrastructure	:	Rs. 101 Crores

64 % of the Capex has been reserved for deposit works and load growth. The losses have been reduced to nearly 11 % during the last 5 years. TPDDL is of the opinion that there is scope for reducing losses further, but reducing losses below 13% would be nightmarish for the reasons mentioned earlier. Therefore, 13 % of Capex has been allotted for AT&C loss reduction.

The investment plan during the period FY 2012-13 to 2014-15 totaling to Rs.1030 Crores is given in table 5.1 as follows:

Table-5.1

| CAPITAL INVESTMENT PLANNING FOR FY 20012-15 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| BUDGET FOR NON DEPOSIT WORKS |  |  |  |  |  |
| 1 | AT&C Loss Reduction Schemes | 2012-13 | 2013-14 | 2014-15 | Total |
| 1.1 | Meter Replacement | 27 | 28 | 38 | 93 |
| 1.2 | HVDS Work | 20 | 15 | 10 | 45 |
| 1.3 | Replacement of LT Bare conductor to LT ABC |  |  |  |  |
| 1.4 | LT ABC for Franchisee/ SPD |  |  |  |  |
| Subtotal for AT&C Loss Reduction |  | 47 | 43 | 48 | 138 |
| 2 | Reliability Improvement Schemes |  |  |  |  |
| 2.1 | Automation Implementation | 8 | 5 | 10 | 23 |
| 2.2 | New Technologies(GIS, Communication, OMS & Smart Feeder) | 12 | 21 | 18 | 51 |
| 2.3 | Safety Related | 8 | 8 | 8 | 24 |
| 2.5 | 11 kV Sick Cable Replacement | 10 | 10 | 10 | 30 |
| 2.6 | Protection & Testing Instruments | 1.5 | 1.5 | 2 | 5 |
| Subtotal for Reliability Improvement |  | 39.5 | 45.5 | 48 | 133 |
| 3 | Load Growth Schemes |  |  |  |  |
| 3.1 | EHV Works |  |  |  |  |
| 3.1.1 | New Grid Substations excluding Deposit Works | 81 | 95 | 92 | 268 |
| 3.1.2 | 66 & 33 kV Lines & Cables |  |  |  |  |
| 3.1.3 | 66 & 33 kV Addition/Augmentation of Bays/Transformers |  |  |  |  |
| 3.1.4 | 11 kV system Augmentation works | 66 | 92 | 54 | 212 |
| 3.1.5 | New Meters | 48 | 49 | 51 | 148 |
| 3.1.6 | LT Works | 10 | 10 | 10 | 30 |
| Subtotal for Load Growth |  | 205 | 246 | 207 | 658 |
| 4 | Infrastructure Development Schemes |  |  |  |  |
| 4.1 | Civil Infrastructure Projects | 5 | 5 | 5 | 15 |
| 4.2 | Information Technology | 17 | 20 | 19 | 56 |
| 4.3 | Administration support | 10 | 10 | 10 | 30 |
| Subtotal for Infrastructure Development |  | 32 | 35 | 34 | 101 |
| Total for Non Deposit Works |  | 323.5 | 369.5 | 337 | 1030 |

Note:

1. Capital Investment for deposit works will be as per requirement.

2. Above Capital Investment does not include IDC.

# 5.1.1	CAPEX FOR LOAD GROWTH

During the MYT period 2007-11 TPDDL has experienced average load growth of 7% , for which capital expenditure of Rs. 522 Cr.  has been incurred. For MYT period 2013-15 the growth in TPDDL area is expected to be higher. A cumulative average growth rate of 8% has been assumed for TPDDL area. To achieve this anticipated load growth an investment of Rs. 658 Cr has been proposed.

# 5.1.1.1	 NEW METERS

It is anticipated that nearly 2.5 lac new consumers would be added during the period 2013-15. In addition to that meters which have become temper prone, faulty/burnt or are tempered would also be replaced. Breakup of additional meters to be installed is given in table 5.1 below:

Table 5.1

| S.No | Type of Meter | No. |  |  |
| --- | --- | --- | --- | --- |
|  |  | 2012-13 | 2013-14 | 2014-15 |
| 1 | Single Phase Meters | 80000 | 87000 | 95000 |
| 2 | Polyphase Meters | 6500 | 6800 | 7000 |
| 3 | LT CT Meters | 3500 | 2400 | 2500 |

# During the MYT period 2013-15, total capital expenditure proposed towards installation of new meters is Rs. 148 Cr.  Year wise breakup of the same is given below:

Table 5.2

| Year | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2012-13 | 48.00 |
| 2013-14 | 49.00 |
| 2014-15 | 51.00 |
| Total | 148.00 |

# 5.1.1.2  NEW GRIDS

Following new grids have been planned to meet the anticipated load growth.

Table – 5.3

| LIST OF PROPOSED NEW GRIDS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SN | Year | Grid | Voltage Level | Deposit* | Non-deposit |
| 1 | 2012-13 | Bawana Phase-2 No-1 | 66 kV | Deposit |  |
| 2 |  | Narela IFC | 33 kV |  | Non-deposit |
| 3 |  | SGTN Phase-2 | 33 kV | Deposit |  |
| 4 |  | ESIC Hospital | 33 kV | Deposit |  |
| 5 |  | Rani Bagh Commercial Centre | 33 kV |  | Non-deposit |
| 6 |  | Pure Earth | 33 kV | Deposit |  |
| 7 | 2013-14 | Kirari | 66 kV |  | Non-deposit |
| 8 |  | Alipur | 66 kV |  | Non-deposit |
| 9 |  | BWN-3 | 66 kV | Deposit |  |
| 10 |  | Burari | 66 kV |  | Non-deposit |
| 11 |  | Bawana-8 | 66 kV | Deposit |  |
| 12 |  | Katputli | 33 kV | Deposit |  |
| 13 | 2014-15 | Lawrence Road | 33 kV |  | Non-deposit |
| 14 |  | Wazirpur-3 | 33 kV |  | Non-deposit |
| 15 |  | Dheerpur | 66 kV | Deposit |  |

# 5.1.1.2	 AUGMENTATION OF EXISTING GRIDS

Augmentation of following grids is proposed during the period 2013-15

Table 5.4

| Grid Augmentation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| S No. | Work | Grid | Rating | Voltage Level | Number |
| 1 | Augmentation of Power Transformer | Gulabi Bagh grid | 16 MVA to 25 MVA | 33/11 kV | 1 |
| 2 | Additionof Power Transformer | GTK grid | 16 MVA (Old) | 33/11 kV | 1 |
| 3 | Additional of Power Transformer | Narela A-7 grid | 25 MVA | 66/11 kV | 1 |
| 4 | Additional of Power Transformer | SMB FC grid | 25 MVA | 33/11 kV | 1 |

The year wise capital expenditure proposed for new grids as well as augmentation of existing grids is given in table 5.5 below:

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2012-13 | 81.00 |
| 2013-14 | 95.00 |
| 2014-15 | 92.00 |
| TOTAL | 268.00 |

Table 5.5

# 5.1.1.3	 AUGMENTATION OF 11 KV NETWORK

Following works are proposed for 11 kV Augmentation works:

      - Installation of additional distribution transformers

      - Augmentation of capacity of existing 11 kV substations

      - Laying of additional 11 kV feeders

The year wise capital expenditure proposed for 11 kV network augmentation is  given in table 5.4 below:

Table 5.6

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2012-13 | 66.00 |
| 2013-14 | 92.00 |
| 2014-15 | 54.00 |
| TOTAL | 212.00 |

District wise allocation of investment proposed for the same is given below:

Table 5.7

| District-wise CAPEX for 11 KV Augmentation (in Rs Cr) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Circle | S No. | Distt. | 2012-13 | 2013-14 | 2014-15 | Grand Total |
| CITY | 1 | MTN | 15.66 | 13.72 | 6.11 | 35.49 |
| METRO | 2 | KPM | 1.03 | 4.94 | 2.47 | 8.44 |
|  | 3 | MGP | 5.90 | 4.32 | 8.25 | 18.47 |
|  | 4 | PPR | 0.53 | 9.86 | 10.26 | 20.65 |
| SUB-URBAN | 5 | BWN | 10.95 | 23.85 | 8.60 | 43.40 |
|  | 6 | NRL | 9.41 | 8.61 | 6.44 | 24.46 |
| TOWN | 7 | CVL | 2.20 | 3.29 | 1.21 | 6.69 |
|  | 8 | MDT | 5.06 | 1.37 | 1.25 | 7.68 |
|  | 9 | SKN | 1.35 | 1.74 | 1.12 | 4.21 |
| URBAN | 10 | BADLI | 1.70 | 6.84 | 2.35 | 10.90 |
|  | 11 | RHN | 5.54 | 8.55 | 3.08 | 17.17 |
|  | 12 | SMB | 5.86 | 5.24 | 3.16 | 14.26 |
| Total |  |  | 66 | 92 | 54 | 212 |

Chart 5.1 gives proposed cumulative investment for load growth vs forecasted peak demand.

Chart – 5.1

# 5.1.2	CAPEX FOR AT&C LOSS REDUCTION

In MYT period 2007-11, capital expenditure for AT&C has been Rs. 293.0 which has resulted in AT&C loss reduction from 18.3% to below 14%. During the control period 2013-15 TPDDL is targeting AT&C loss reduction from 13% to 12.25%.  To achieve this target an investment of Rs. 138 Crores has been proposed. This investment is proposed under following heads:

# 5.1.2.1	REPLACEMENT OF METERS

Some of the existing meters are required to be replaced for the following reasons:

- Meters booked under enforcement

- Faulty/Burnt meters

- Temper prone meters.

Estimated number of meters required to be replaced for above mentioned reasons is given in table 5.8 below.

| S.No | Type of Meter | No. |  |  |
| --- | --- | --- | --- | --- |
|  |  | 2012-13 | 2013-14 | 2014-15 |
| 1 | Single Phase Meters | 60000 | 65000 | 75000 |
| 2 | Polyphase Meters | 3000 | 3000 | 3000 |
| 3 | LT CT Meters | 1000 | 700 | 700 |

Table 5.8

# The year wise estimated capital expenditure for replacement of meters is given in table 5.9 below:

Table 5.9

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2012-13 | 27.00 |
| 2013-14 | 28.00 |
| 2014-15 | 38.00 |
| TOTAL | 93.00 |

# 5.1.2.2	LTABC and HVDS WORKS

No major HVDS work is anticipated during MYT period 2013-15. In LTABC major work anticipated in extension of existing LT ABC network due to new dwelling units in the area and replacement of bare conductors in few pockets. The year wise capital investment proposed for the same is given in table 5.10 below.

Table 5.10

| Period | Capital Expenditure (Rs. Cr.) |
| --- | --- |
| 2012-13 | 20.0 |
| 2013-14 | 15.0 |
| 2014-15 | 10.0 |
| TOTAL | 45.0 |

District wise allocation for LT ABC is given in Table 5.11.

Table 5.11

| Capex for LTABC |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CIRCLE | DISTRICT | ZONE | 2012-13 | 2013-14 | 2014-15 | Total |
| CITY | Moti Nagar | 1301 | 0.39 | 0.16 | 0.10 | 0.65 |
| METRO |  | 1302 | 0.55 | 0.31 | 0.21 | 1.07 |
|  |  | 1303 | 1.17 | 0.93 | 0.62 | 2.72 |
|  |  | 1304 | 0.29 | 0.05 | 0.03 | 0.36 |
|  | Keshav Puram | 502 | 0.30 | 0.06 | 0.04 | 0.40 |
|  | Pitampura | 504 | 2.80 | 2.56 | 1.71 | 7.06 |
|  |  | 508 | 1.85 | 1.61 | 1.07 | 4.53 |
|  |  | 510 | 0.47 | 0.23 | 0.16 | 0.86 |
|  |  | 530 | 0.58 | 0.34 | 0.23 | 1.15 |
| SUB-URBAN | Bawana | 512 | 1.99 | 1.75 | 1.17 | 4.91 |
|  | Narela | 514 | 1.24 | 1.00 | 0.67 | 2.91 |
|  |  | 517 | 1.44 | 1.20 | 0.80 | 3.44 |
| URBAN | Badli | 507 | 0.43 | 0.19 | 0.13 | 0.76 |
| TOWN | Model Town | 402 | 1.76 | 1.52 | 1.01 | 4.29 |
|  |  | 412 | 1.05 | 0.81 | 0.54 | 2.41 |
|  |  | 413 | 0.59 | 0.35 | 0.23 | 1.17 |
|  |  | 415 | 0.32 | 0.08 | 0.05 | 0.45 |
|  | Shakti Nagar | 421 | 0.83 | 0.59 | 0.39 | 1.81 |
|  |  | 422 | 0.32 | 0.08 | 0.05 | 0.45 |
|  |  | 423 | 0.66 | 0.43 | 0.28 | 1.37 |
|  |  | 425 | 1.00 | 0.76 | 0.51 | 2.26 |
| Total |  |  | 20.00 | 15.00 | 10.00 | 45.00 |

Proposed year wise investment for AT&C Loss Reduction (Cumulative) and corresponding targeted AT&C Loss Reduction is depicted in Chart – 5.2.

Chart – 5.2

# 5.1.3	CAPEX FOR RELIABILTY IMPROVEMENT

During the control period 2013-15 TPDDL proposes to further strengthen the network, introduce new technologies to enhance customer satisfaction in terms of safe and reliable supply of electricity.  To achieve this same an investment of Rs. 119 Crores has been proposed.

# 5.1.3.1 NEW TECHNOLOGIES

Further reliability improvement will br done by inclusion of new technologies. Following works are proposed in MYT period 2013-15:

- Automation

Following works are proposed to be done during MYT period:

    - It is proposed to upgrade existing SCADA, EMS and DMS system due to addition of new grids and expansion of 11 kV network for the reliability improvement by induction of new technologies. Investment under this head is proposed at 12 Cr. during the MYT period.

    - Network planning requires extending LT level planning integration with respect to GIS database. For the same upgrade and inclusion of new license is required. Investment under this head is proposed at 1 Cr during MYT period.

    - At present MTTR for 11 KV distribution system is above two hours and it is proposed to include Distribution Automation work by addition of RTU automation and Fault Passage Indicator to reduce the outage time to  less than 30 minutes. Investment under this head is proposed at 9 Crores during MYT period.

Item-wise break-up of Capital Investment proposed is given in table 5.12 (amount in Rs Cr):

Table— 5.12

| S No. | Item | FY 12-13 | FY 13-14 | FY 14-15 |
| --- | --- | --- | --- | --- |
| 1 | Grid Substation Automation | 0.80 | 0.50 | -- |
| 2 | SACDA/EMS DMS Systems | 0.20 | 0.50 | 10.00 |
| 3 | NPAG | 1.00 | -- | -- |
| 4 | Distribution Automation | 6.00 | 2.00 | 1.0 |
| Total |  | 8.00 | 3.00 | 11.00 |

- Communication Network

Following works are proposed to be done during MYT period:

    - Due to ring architecture (RPR topology), data traffic is originating and getting terminated in single station and any breakdown in physical media results in communication failure for multiple sites connected through that site. Any breakdown in fibre between tapping point to FMS (Fibre management System box) results in communication failure of that particular node and all other connected nodes. To avoid such situations it is proposed to lay redundant approach cable from alternative nearest tapping point to FMS. Investment under this head is proposed at Rs. 3.50 Cr. during MYT period.

    - TPDDL has taken 2 pairs of fiber on lease basis from M/s TATA Teleservices Ltd. for 73.53 Kms. This primarily forms our core ring and one sub ring. However due to the unavailability of spare fibers on these routes and to eliminate 3rd party dependency, it is required to create TPDDL own fibre network on these rings. Investment under this head is proposed at Rs. 4.50 Cr. during MYT period.

    - As all grids are unmanned and there is lot of public interaction in district offices. A surveillance system will help to protect people and assets and minimize liabilities and avoid trivial lawsuits. Investment under this head is proposed at Rs. 4 Cr. during MYT period.

    - Power plant are connected with Communication equipment’s to provide -48V dc supply and for over voltage protection. Existing power plants (Delta make) are now obsolete and OEM has expressed their inability to continue maintenance support. It is therefore required to upgrade existing power plants with remotely managed power plants. Investment under this head is proposed at Rs. 45 lacs during MYT period.

    - To ensure communication reliability of mission critical services, communication equipment are commissioned with separate battery banks to provide back up of 8 hrs. So that communication remains unaffected in case of local supply failure /Grid failure. Most of these batteries need replacement as they are in services for more than 6 years and unable to provide desired back up. Investment under this head is proposed at Rs. 30 lacs during MYT period.

    - In order to provide WAN connectivity for IT and operational applications, TPDDL is   having approximately 250 kms of fiber network connecting unmanned grids, district offices, consumer care centers and zonal offices. Investment under this head is proposed at Rs. 1.90Cr. during MYT period.

    - TPDDL district offices and 11 kV feeders emanating from DTL grids are connected to TPDDL SCADA system by installing E/F converter at DTL grid RTU and nearby TPDDL grid RTU. Any breakdown in communication from DTL end require physical visit to DTL site as existing E/F converters are not remotely controlled. Hence by replacing existing converters by IP based converters it will be possible to troubleshoot breakdowns from central control room.  Investment under this head is proposed at Rs. 20 lacs during MYT period.

    - At present TPDDL sites where single service is running i.e. only SCADA or enterprises, are connected through media converters , are to be connected through mux so that in future all operational and enterprises application are accessible pan TPDDL .Also last mile connectivity can be provided for future upcoming projects (Smart grid, MWM etc.). Investment under this head is proposed at Rs. 50 lacs during MYT period.

    - At present we have installed SDH mux (STM-16 for core ring & STM-4 for sub rings) in our network. To cater future bandwidth requirements (data, voice, video etc.)  and to increase network robustness, it is required to upgrade existing hardware/technology. Presently IP-MPLS,DWDM,LTE and STM-64 are under evaluation for TPDDL network. Investment under this head is proposed at Rs. 9 Cr. during MYT period.

Item-wise break-up of capital Investment proposed is given below in table 5.13

Table—5.13

| Information Technology (IT) (Amount in Lacs) |  |  |  |  |
| --- | --- | --- | --- | --- |
| S No. | Name of Scheme / Activity | FY' 12-13 | FY' 13-14 | FY' 14-15 |
| 1 | Secondary Data Center | 100 | 50 | 50 |
| 2 | Disaster Recovery Hosting | 0 | 300 | 0 |
| 3 | SAP | 200 | 200 | 200 |
| 4 | Integrated Power Procurement Solution | 250 | 0 | 0 |
| 5 | Adobe Forms & approval through mobile devices | 0 | 0 | 0 |
| 6 | Security Information & Event Management | 0 | 50 | 50 |
| 7 | E - Biz | 0 | 60 | 0 |
| 8 | PC/ Laptop (hardware part) | 300 | 350 | 350 |
| 9 | UPS (hardware part) | 10 | 50 | 50 |
| 10 | Procurement of new servers (hardware part) | 0 | 150 | 150 |
| 11 | Network (Switches, Router, LAN/WAN) (hardware part) | 20 | 40 | 60 |
| 12 | Printers / Scanners / Plotters (hardware part) | 5 | 15 | 25 |
| 13 | Storage (hardware part) | 0 | 30 | 50 |
| 14 | Microsoft Enterprise Agreement (software item) | 0 | 100 | 0 |
| 15 | New Technology (software item) | 5 | 25 | 25 |
| 16 | Security (software item) | 0 | 0 | 50 |
| 17 | Router NMS for traffic monitoring | 40 | 0 | 0 |
| 18 | Implementation of IFRS in SAP | 100 | 0 | 0 |
| 19 | Upgradation of Call Centre | 200 | 0 | 0 |
| 20 | Tape Library (hardware part) | 0 | 0 | 40 |
| 21 | Enterprise Application Integration (EAI) | 250 | 300 | 100 |
| 22 | PI | 250 | 100 | 0 |
| 23 | Enterprise Management Tool | 0 | 200 | 300 |
| 24 | Data Archival Solutions | 0 | 0 | 200 |
| 25 | Oracle License | 0 | 0 | 200 |
|  | Total | 1730 | 2020 | 1900 |

- Geographical Information System

GIS has been implemented for mappig of distribution assets and integarted with SAP-PM, SAP-FICO and SAP-ISU which is being used for asset management, scheme preparation, release of instant new connection, dues recovery, street light mapping with Pole no. etc. It is also integrated with Distribution Management system (DMS) for 11KV network operation and outage management system for ouatages at LT and/or consumer end. GIS data is a pre-requisite element for operation of OMS.  Distribution asset repository and its network modeling in GIS is also used for capital investment planning. GIS has been integrated with SAP-PM, SAP-ISU, SAP-FICO, OMS along with manual interface. It is necessary to upgrade GIS system to have seamless integration with above business system to improve upon operational efficiency and productivity enhancement. To keep pace with the software life cycle of OEM, it is necessary to upgrade the software for enhanced features.  Investment under this head is proposed at Rs. 5 Cr. during MYT period.

Every distribution asset installtion in field needs to get updated in GIS with respect to lattitude, longitude. To update the same, PDA device is used having GIS map for updation of new, moved, retired assets in GIS system. To improve the updation of distribution assets installed by various users like
capturing of new consumers by meter management group,
new assets installation by Project group & zones and
asset movement and network changes by Zones. 
Usage of PDA provides fast updation of the above in GIS which in turn improve the processes of OMS and Asset management. Investment under this head is proposed at Rs. 1.5 Cr. during MYT period.

Item-wise break-up of capital Investment proposed is given in table 5.14:

Table—5.14

| Geographical Information System (GIS) (Amount in Rs Lacs) |  |  |  |  |
| --- | --- | --- | --- | --- |
| S No. | Name of Scheme / Activity | FY' 12-13 | FY' 13-14 | FY' 14-15 |
| 1 | Upgrade of GIS Software | 0 | 300 | 200 |
| 2 | PDA | 50 | 50 | 50 |
|  | Total | 50 | 350 | 250 |

- Outage Management System

Outage Management system has just been implemented in one circle and by the end FY 11-12 it shall be implemented across TPDDL. This shall ensure centralized control of the field crew for no supply crew which shall optimize the crew requirement. So far following are the visible improvements.

- Street light MTTR has improved to 1.09 days from 2 days last year.

- No supply complaints resolution within 2 hrs has improved to 96% from 80% last year.

- No. of complaints registered for Motinagar are 30% less as compared to last year due to information availability at CRM due to integration of SRM, OMS, GIS and SCADA/DMS.

The system deployed lacks one architectural aspect. Hot failover feature is missing at present. To make this hot failover capable the system hardware and application software needs to be upgraded.

Outage Management system has been implemented in one circle and by the end FY 11-12 it shall be implemented in all circles of TPDDL. This shall ensure centralized control of the field crew for no supply crew which shall optimize the crew requirement. It will maximize efficiencies across the enterprise through effective planning, scheduling, routing and dispatching of work. It will also enable the below mentioned activities:-

- New meter installation/Meter removal

- Meter Exchanges

- Trouble call/Restoration/emergency orders

- Credit Collections

- Periodic Maintenance

- Effective complaint redressal

Investment under this head is proposed at Rs. 5.5 Cr. during MYT period.

Item-wise break-up of Capital Investment proposed is given in table 5.15:

Table—5.15

| Outage Management System (OMS) (Amount in Rs Lacs) |  |  |  |  |
| --- | --- | --- | --- | --- |
| S No. | Name of Scheme / Activity | FY' 12-13 | FY' 13-14 | FY' 14-15 |
| 1 | Outage Management System (OMS) | 0 | 200 | 0 |
| 2 | Mobile Workforce Management (MWM) | 350 | 0 | 0 |
|  | Total | 350 | 200 | 0 |

- Smart Feeder

To bring about the improvements in reliability, AT&C loss reduction and improving customer service in 2003 NDPL deleberated with various global utilities and consultants and prepared its automation raodmap. Under the Automation roadmap, NDPL so far has implemented SCADA/DMS with  GSAS and DA, AMR, GIS, SAP, OMS to name a few. There had been both tangible and non tangible benefits. Two major benefits are listed below:

1. SAIDI has improved from 40 to 6 hrs.

2. AT&C loss reduced from 53.3 to 13.2 %.

However to sustain the current level of progress and keep pace with the global technology and improvement trends, TPDDL propose to implement excellent Smart Grid technologies. For this purpose, TPDDL is shortly going to appoint a renowned US consultant for drawing their Smart Grid Roadmap. Payment to the consultant shall be made by USTDA through the sanctioned grant.

The intended benefits of the same are:

- Keep consumer engaged which will contribute to voluntary participation, energy usage and reduce peak power demand.

- Connect/Disconnect remotely will ensure better revenue management and aid in further reduction of AT&C Loss.

- Smart Demand Response has a potential of peak saving of 130MW.

- Continuously strive to mitigate technology obsolescence.

Investment under this head is proposed at Rs. 25 Cr. during MYT period.

# 5.1.3.2	 SAFETY RELATED

Installations which pose immediate threat to safety of the operating personnel, network equipments, and general public at large will be concentrated upon at the initial stage. Following works are proposed to make the installations safe:

- Installation of MCCB for LT protection at secondary side of transformer.

- Providing and connecting Earthing for all network equipments.

- Providing guard wire on 11KV bare O/H network.

- Refurbishment of RMU'S.

Investment under this head is proposed at Rs. 24 Cr. during MYT period.

# 5.1.3.3	11 kV SICK CABLE REPLACEMENT

There are 11 kV underground cables which are more than 25 years old and are prone to frequent faults. These cables are proposed to be replaced to improve the reliability of the system. Capital Investment for Reliability Improvement is proposed on the basis of cable failure for the districts and is given in Table – 5.16

Table – 5.16

| CAPEX FOR SICK CABLES (in Rs Cr) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| CIRCLE | District | FY 12-13 | FY 13-14 | FY 14-15 | Total |
| CITY | MTN | 1.4 | 1.4 | 1.4 | 4.2 |
| METRO | PPR | 1.6 | 1.6 | 1.6 | 4.8 |
| SUC | BWN | 0.1 | 0.1 | 0.1 | 0.3 |
|  | NRL | 0.6 | 0.6 | 0.6 | 1.8 |
| TOWN | CVL | 1.9 | 1.9 | 1.9 | 5.7 |
|  | MDT | 1.8 | 1.8 | 1.8 | 5.4 |
|  | SKN | 1.0 | 1.0 | 1.0 | 3.0 |
| UC | BDL | 0.4 | 0.4 | 0.4 | 1.2 |
|  | RHN | 0.4 | 0.4 | 0.4 | 1.2 |
|  | SMB | 0.5 | 0.5 | 0.5 | 1.5 |
| Total |  | 10 | 10 | 10 | 30 |

# 5.1.3.4 	PROTECTION & TESTING OF INSTRUMENTS

Major items proposed to be procured for protection and testing purposes includes:

- Spares for existing relays

- Retrofitting of relays

- Line differential relays

- Relay Testing kits

- Meggar

- Winding machine for transformers

Investment under this head is proposed at Rs. 5 Cr. during MYT period.

The year wise investment for Reliability Improvement (Cumulative) and corresponding targeted Reliability Indices is depicted in Chart – 5.3

Chart – 5.3

# CREATION OF INFRASTRUCTURE FACILITIES AND ADMINISTRATIVE BUILDING

      - Civil Infrastructure

It is planned to construct new building for Corporate Office, Commercial offices as well as renovation of exiting district and zonal offices.

      - Information Technology

It is proposed to upgrade the Secondary Data Center, SAP, existing Call Centers and other IT infrastructure. Additional Servers, Desktops/Laptops, printers, security software is also proposed.

      - Administration Support

New vehicles, office infrastructure, security systems, stationary items etc are proposed to be procured for administration support.

Chart 5.4 depicts the proposed investments for Infrastructure Schemes from 2013-15

Chart 5.4

Benefit Head wise investment planned for the period of 2012-2015 is depicted in Chart – 5.5.

Chart – 5.5

# 5.2	CAPITALIZATION SCHEDULE

The details of Capital Investment by TPDDL and the assets capitalized against these investments are given below:

Table – 5.17

| Year | Capital Investment (Rs Cr) | Asset Capitalised (Rs Cr) |
| --- | --- | --- |
| 2007-08 | 245.12 | 264.45 |
| 2008-09 | 288.54 | 337.16 |
| 2009-10 | 374.10 | 375.80 |
| 2010-11 | 465.50 | 390.0 |
| 2011-12 | 250.00 | 378.32 |
| Total | 1373 | 1367 |

For the period 2012-13, the proposed capital investment and asset capitalization is given in the Table below:

Table 5.18

| Year | Capital Investment (Rs Cr) – Including Int. | Asset to Capitalize (Rs Cr) |
| --- | --- | --- |
| 2012-13 | 417.41 | 359.37 |
| 2013-14 | 470.87 | 432.53 |
| 2014-15 | 445.34 | 450.44 |
| Total | 1333.6 | 1242.3 |

# 5.3	FINANCING PLAN

TPDDL proposes to fund the capital expenditure through a mix of consumer contribution, depreciation, internal accruals and domestic loans in the same order of priority.

# CHAPTER – 6

# QUALITY IMPROVEMENT PLAN

# 6.1	 TRANFORMER & FEEDER FAILURE RATE

At the time of take over distribution transformer failure rate was as high as 8.3%, which has been brought down to 1.10 % as on 31st March 2011. Similarly, interruption per 11 kV feeders has been brought down to 2.49 hrs hour per feeder from 9.34 hours per feeder.

Table – 6.1

| Transformer and Feeder Failure Rate |  |  |  |  |
| --- | --- | --- | --- | --- |
| Particulars | 2007-08 | 2008-09 | 2009-10 | 2010-11 |
| No. of 11kv feeders | 677 | 718 | 737 | 781 |
| No of feeder tripping at 11kv (Due to faults) | 5111 | 5816 | 4984 | 4242 |
| Total duration of feeders tripping in Hours. | 47755 | 8724 | 8656 | 10555 |
| Interruptions per feeder (in hours) | 9.34 | 1.5 | 1.74 | 2.49 |
| Total capacity of DTs (MVA) | 3233 | 3478 | 3771 | 4160 |
| DT failure (MVA) | 53.38 | 44.74 | 58.25 | 45.59 |
| DT failure rate (%) W.R.T. Installed capacity | 1.65 | 1.29 | 1.54 | 1.10 |

TPDDL further plans to bring down the distribution transformer failure rate to 0.90 % and interruption per 11 kV feeders to 30 minutes per feeder as per the schedule given below:

Table 6.2

| Particulars | 2012-13 | 2013-14 | 2014-15 |
| --- | --- | --- | --- |
| Interruptions per feeder (in hours) | 1.5 | 1.2 | 0.5 |
| DT failure rate (%) w.r.t. Installed capacity | 1.00 | 0.95 | 0.90 |

# 6.2	FREQUENCY VARIATIONS:

The TPDDL shall maintain the supply frequency as per the Indian Electricity Grid Code (the present values being between 49.0 and 50.5 Hz), as amended from time to time.

# 6.3	VOLTAGE UNBALANCE:

The TPDDL shall ensure that the voltage unbalance does not exceed 3% at the point of commencement of supply.